Table 1: PPA PROJECT SPECIFIC INFORMATION

[Note: Fill in table below with the project-specific information for each solar facility.]

[Note for rooftop solar – given the requirement for either a PVSyst or a Helioscope production models, please use the parameters indicated within this specification sheet as guidance toward Helioscope-generated models.]

| Project/Site Information |  |  |
| --- | --- | --- |
| Project Name | [ Project / Site Name ] |  |
| Project Address | [ Physical Address ] |  |
| Project Site Specifications | Unit | Value |
| Latitude | deg. | [ xx.xx ] |
| Longitude | deg. | [ xx.xx ] |
| Land Area | acres | [ ] |
| Interconnection Facility Specifications | Unit | Value |
| Interconnection Type | Transmission or Distribution | [ ] |
| Interconnection Voltage, Nominal | kV | [ ] |
| Maximum Voltage (Vmax) per PJM Standard Schedule Minimum Voltage (Vmin) per PJM Standard Schedule | kV | [ ] Vmax [ ] Vmin |
| Power Factor Capability (PF Lag), Lagging, at Point of Interconnection, Minimum |  | 0.95 PF Lag |
| Power Factor Capability (PF Lead), Leading, at Point of Interconnection, Minimum |  | 0.95 PF Lead |
| Generator Tie Line Length | miles | [ ] |
| Main Power Transformer Capacity | MVA | [ ] |
| AC Collection System Voltage, nominal | kV | 34.5 |
| Solar Facility Specifications | Unit | Value |
| Required Real Power Output at POI at Vmax | MWac | [ ] |
| Required Real Power Output at POI at Vmin | MWac | [ ] |
| DC Nameplate Capacity | MWp | [ ] |
| DC Collection System Voltage, Maximum | Vdc | 1,500 |
| Module Mounting System Type | Single Axis Tracking or Fixed Tilt | [ ] |
| Modeled Annual Energy Production Year 1, under Typical Conditions, at Point of Metering | MWh | [ ] |

- The “Base Case Model” requested in Section D “Technical Info” of the Information Form Addendum shall be comprised of a PVSyst model and an 8760 hour predictive energy production file for year 1 based on the following specifications.

- Base Case Model Requirements

The “Base Case Model” shall be comprised of a PVSyst model and an 8760 hour predictive energy production file for year 1 which is representative of the equipment configuration, losses, and operating behavior based on historical/typical weather data using mathematical models as contained in the PVsyst software.  Post-processing using Microsoft Excel is acceptable only for adding 8760 hourly results from separate PVsyst variants and applying the POI Grid Limit and as described in Section B.13 below. The PVSyst Model and associated 8760 shall follow parameters in Table 2 and should be provided with your bid submission.

The Base Case Model for proposals shall include the following at the minimum:

- The latest version of the PVsyst Photovoltaic Software at time of contract or if that’s not available, the closest subsequent version..

- The latitude and longitude of the Project Site.

- The typical-year solar resource and weather dataset of record for the Facility using the latest version of SolarAnywhere and select the TGY Typical Year Option.

- The Project Site albedo assumption for monthly averages, sourced from NREL NSRDB PSM website (nsrdb.nrel.gov), Dataset - USA & Americas (30, 60min / 4km / 1998 – 2023 or the latest year).

- The use of the Perez transposition model.

- The orientation of the PV arrays represented in the Facility, including row or tracker spacing, tilt angle (fixed-tilt systems only), tracking range (tracker systems only), azimuth angle, axis tilt angle, axis height above ground, minimum height above ground (fixed-tilt systems only), collector width, and ground-coverage ratio (GCR).

- Equipment types and quantities for the PV modules and inverters comprising the Facility.

- Complete set of native files, including but not limited to the list below, utilized in the software model so the Base Case Model can be recreated. A third-party (PVEL, RETC, DNV or other third party approved by Owner) validated PV module .PAN file shall be provided or that used in the Base Case Model.  An Inverter .OND file shall include three (3) efficiency curves and account for auxiliary load losses required during the inverter operation.

  - .pan – PV Module performance model created by either the module supplier or a 3rd party lab.

  - .ond – Inverter performance model

  - .met – Weather data file including its source

  - .prj – Unique project definition file

  - .VC – Provide all variant files defined within PVsyst describing the cases being evaluated.

  - .shd – Near shading file, generated within PVsyst

  - .sit – Site definition file containing the references to the specific weather file, the shading scene and other parameters

  - .hor – Describes the distant horizon features, such as, mountains that may impose shading on the site.

- The configuration of the PV arrays represented in the Facility, including the number of modules, the number of modules per string, strings per inverter, number of inverters, and DC/AC ratio.

- Facility availability shall be set to 100%.

- All transformer and auxillary nighttime losses shall be excluded in the Base Case Model.

- The Base Case Model shall include all daytime auxiliary loads and losses required for the facility normal operation including but not limited to those associated with the onsite transformers, trackers, SCADA, weather stations and substation.  These loads and losses shall be clearly accounted for in the Base Case Model.

- In addition to that stated in Section I, specification of post-processing calculations may be implemented after the modeling software output is calculated to model tracker optimizing programs like NEXTracker’s TrueCapture and ATI’s SmarTrack and to account for East-West Slope production adjustments, if applicable.

- The 8,760 Expected Hourly Energy Production values (kWh) over a Typical Year, computed using the above and assuming a P50 Probability of Exceedance.

- The Expected Annual Energy Production computed by summing the 8,760 Expected Hourly Energy Production values described above.

- Bidders shall verify that the quantity of inverters proposed while generating power will maintain the Power Factor as specified in Table 1 and also produce the real power name plate rating MWac at the POI for a “Distribution” connected facility.  For a “Transmission” connected facility, a combination of inverters and cap bank may be used to ensure the real power nameplate rating MWac at the POI is maintained.

- If the inverter’s capacity is temperature dependent, the Base Case Model shall account for the generation loss due to temperature derating.

- Near Shadings, PVsyst  shall be used to model row-to-row shading (tracker and fixed tilt) and significant near-field shading such as trees.  The height of the trees or shading walls is to be 100 feet,  The shading model shall be representative of the proposed site layout including the remaining vegetation within and surrounding the site boundary post construction.  If there are significant changes in elevation at the Project Site, such as rolling hills, the PVsyst shading scene shall include site specific topography.

- If project specific IAM losses are used, provide the third party (PVEL, RETC,  DNV or other third party approved by Owner) analysis to support entry to PVsyst.

- The PVsyst input for “Lower temperature for Absolute Voltage limit” is to be determined using the NERC method documented in, “NERC_Calculating Extreme Cold Weather Temperature_EOP-012”, dated Sep-2022.  PVsyst needs to be able execute with this temperature specified.

- String length (Modules/String) is to be set per NEC 690.7(A)(3).  The conservative string length from the Berkeley Lab DuraMAT on-line tool (pvtools.lbl.gov/string-length-calculator) is to be used.

- If the Project Site experience regular high wind speeds, production losses due to tracker’s wind-stow shall be included in the Base Case Model.

- Spectral correction shall be included if thin film PV modules are used.

- Modeling assumptions and basis specific to bifacial PV modules, if applicable.

Table 2: PVSyst Assumption/Parameter Requirements: [Changes Highlighted]

| PVSyst Parameter | Value | PVSyst Parameter | Value |
| --- | --- | --- | --- |
| Transposition Model | Perez | Module Quality Losses Incl: - Positive Tolerance - Inerter MPP Tracking - First Year Module Degradation using mid year value | PERC TOPCon Thin Film(%) 104.99 a) 0.00% 0.00% -284.45 b) +0.50% +0.50% 273.89 c) 0.5/2 = +0.25% 0.7/2=+0.35% -108.95 PVsyst Input: +0.75% +0.85% 15.41 Thin Film 4th Order Coef. DC/AC@POI Indep. Var |
| Meteo Data | Latest Version of SolarAnywhere at Contract Signing | Module Mismatch Losses | 2.0% |
| Albedo | NREL NSRDB PSM Database | Horizon | Meteonorm or PVGIS |
| Array Soiling Losses | 2.0% | AC Losses (Iron Losses) | 0.2% for one level of transformation 0.3% for two levels of transformation |
| Thermal Loss Uc | 29 W/m2K For monofacial PV modules. Bifacial PV modules use the same unless manufacturer recommends Uc to be used | AC Losses (Res/Ind) | 0.9% for one level of transformation 1.3% for two levels of transformation |
| Thermal Loss Uv | 0 W/m2K / m/s | AC Losses (Conductor) | 1.5% for string inverters 1.5% for central inverters |
| DC Wiring Ohmic Losses at STC | 1% for string inverters – in arrays 1.5% for co-located String Inverters 1.5% for central inverters | Daytime Auxiliaries Losses (including SCADA, trackers, weather stations, and substation) | Unless supporting data is provided: Only use PVsyst input “Continuous auxiliary loss” Trackers not Self-Powered use 0.1% of POI MWac Trackers Self-Powered use 0.05% of POI MWac Fixed-Tilt use 0.05% of POI MWac |
| Light Induced Degradation (LID) Plus Sub-Hourly Clipping Loss * If DC/AC @POI <1.0, set the input equal to the value for DC/AC @POI=1.0. | 4th Order Polynomial Equation: Independent Variable (x) = DC/AC @POI * PERC(%) TOPCon(%) a0 105.74 104.74 a1 -284.45 -284.45 a2 273.89 273.89 a3 -108.95 -108.95 a4 15.41 15.41 | Grid Power Limitation | Refer to the “Required Real Power Output” and “Power Factor” in Table 1 above |
| IAM Losses | 3rd Party Report or Fresnel with AR Coating | Tracker Rotation | Tracker specific |
| Bifacial Rear Shading Loss | 20% for Trackers 20% for Fixed-Tilt | Bifacial Mis-Match Loss | 10% for Trackers 10% for Fixed-Tilt |
| Bifaciality Factor | Median PV Module Datasheet Value | Bifacial Transparency | 0% Otherwise, provide 3rd Party Supporting Data |
| Ground Albedo (Bifacial Rear Side) | NREL NSRDB PSM database Select USA / (…1998-2023) | Circumsolar Irradiance | Separate Component |
| String Mismatch | 0.1% | Back Tracking | PERC / TOPCon – Yes Thin Film – No Fixed-Tilt – Not Applicable |